## Calculations
Dimensioning of cables
18.03.2022/Cjü
PRECONDITIONS
Cable properties
| A | 0.34 | mm² | Cross-section of the cable surface [m2]
| rho | 1.72e-08 | Ohm m | Specific resistance of copper [Ωm]
| alpha | 0.0039 | 1/K | Temperature coefficient of copper [1/K]
Ambient conditions
| T0 | 20 | °C | Reference temperature [°C]
| T | 80 | °C | Cable temprature [°C]
Cable load
| I | 2.5 | A | Load current [A]
| this corresponds to: | 60 | Watt
Permissible length of cable
Voltage drop on the cable (max. permissible)
| deltaV | 0.2 | V | Voltage drop on the cable [V]
Permissible length of cable
| L | 0.64076 | m | Permissible length of cable [m]
Resulting voltage drop
Cable length
| L | 0.43 | m | Cable length [m]
Resulting voltage drop
| deltaV | 0.13422 | V | Voltage drop on the cable [V]
See manual LMS5xx, chapter 6.5.3 LMS5x1 Outdoor cable cross-section